## README
Kenya as East Africa's low-carbon industry hub - strategy model
Question: Should Kenya position itself as East Africa's hub for energy-intensive, low-carbon industry (data centres first), and what would it take?
How to read this workbook
Summary Headline outputs, all linked. Start here.
Inputs Every assumption, tagged [S] sourced or [A] analyst assumption. Change blue cells; everything recalculates.
Grid Peak demand versus firm, evening-capable supply, 2026-2032, in three supply cases (Stress / Base / Favourable).
Hub Data-centre demand in three hub cases (Status quo / Targeted / Ambitious) and the size of the prize in 2030.
Matrix Reserve margin, firm-MW gap and connectable load for every supply x hub combination.
UnitEconomics Tenant cost per kW-month and an illustrative 44 MW campus (NPV, IRR, break-even fee, sensitivities).
Levers Five levers sized against the 2030 firm-capacity gap, with indicative annual cost.
Screen Judgement-based screen of which industries fit Kenya's evening-constrained grid.
Sources Source register (S1-S27) and the conflicts between sources and how each is resolved.
Checks Integrity checks; all should read TRUE.
Colour code: blue = input; black = formula; green = link from another sheet; yellow fill = key lever.
Limits you should know about
1. Several inputs come from press reports quoting Kenya Power / EPRA briefings, not primary datasets. Confirm against EPRA statistics before publishing.
2. Colocation pricing, utilisation, opex and the discount rate are analyst assumptions because no public Kenyan price data was available.
3. 'Firm' means available at the 6-10pm peak. Solar is therefore counted at 0%; storage at its rated MW for a 4-hour peak.
4. A negative reserve margin means unserved peak unless emergency capacity is procured; it sizes the response, it does not forecast blackouts.
5. The campus case is pre-tax and unlevered and meant to show what price or cost of capital a campus needs, not to value a specific project.

## Summary
Summary of results - Kenya as East Africa's low-carbon industry hub
All figures are live links to the calculation sheets. Scenario definitions are on the Inputs sheet.
1. Grid headroom (supply cases) | Stress | Base | Favourable
Peak demand, Jun 2026 (MW) | 2514 | 2514 | 2514
Firm available capacity, Jun 2026 (MW) | 2476.29 | 2597.9676 | 3035.1522
Spare MW, Jun 2026 | -37.71 | 83.9676 | 521.1522 | Base: the whole national spare margin
Reserve margin 2027 (no hub) | -8.796% | 8.835% | 26.95%
Reserve margin 2028 (no hub) | -8.186% | 2.193% | 23.8%
Reserve margin 2030 (no hub) | -18.94% | -2.78% | 25.38%
Reserve margin 2032 (no hub) | -30.5% | -6.107% | 31.54%
New firm MW needed per year just to hold the margin, 2030 | 253.3533 | 197.391 | 145.5135
2. The prize (hub cases, 2030) | Status quo | Targeted hub | Ambitious hub
Kenya data-centre IT capacity (MW) | 74 | 222 | 370
Share of Africa capacity | 4% | 12% | 20%
Infrastructure-fee revenue pool ($m/yr) | 99.9 | 299.7 | 499.5
Build investment 2026-2030 ($bn) | 0.232 | 1.416 | 2.6
Operational jobs | 317.1429 | 951.4286 | 1585.7143
Hub load added to grid (MW) | 0 | 155.4 | 310.8
Hub-attributable firming cost ($m/yr) | 0 | 29.3481 | 58.6962
Firming cost as % of fee revenue | 0% | 9.792% | 11.75%
Energy drawn by the data-centre estate (TWh/yr) | 0.68065 | 2.042 | 3.4033
3. Reserve margin in 2030 (rows: supply case; columns: hub case) | Status quo | Targeted hub | Ambitious hub
Stress supply | -18.94% | -22.46% | -25.69%
Base supply | -2.78% | -7.237% | -11.3%
Favourable supply | 25.38% | 19.32% | 13.81%
4. Firm MW needed in 2030 to reach the minimum reserve margin | Status quo | Targeted hub | Ambitious hub
Stress supply | 989.7062 | 1160.6462 | 1331.5862
Base supply | 413.3264 | 584.2664 | 755.2064
Favourable supply | 0 | 0 | 0
5. Firm MW needed in 2030 to reach the target reserve margin | Status quo | Targeted hub | Ambitious hub
Stress supply | 1160.7196 | 1339.4296 | 1518.1396
Base supply | 575.0353 | 753.7453 | 932.4553
Favourable supply | 0 | 0 | 40.1179
6. Connectable IT MW at the minimum reserve margin | 2027 | 2028 | 2030
Stress supply | 0 | 0 | 0
Base supply | 0 | 0 | 0
Favourable supply | 387.4305 | 331.2543 | 407.0054
7. Tenant cost per IT kW-month ($) | Stress | Base | Favourable
Infrastructure fee | 110 | 150 | 200
Grid power | 112.42 | 91.98 | 66.43
Evening self-supply premium | 22.0331 | 22.0331 | 22.0331
All-in cost | 244.4531 | 264.0131 | 288.4631
Power share of all-in cost | 55% | 43.18% | 30.67%
Power-price gap vs Ethiopia-linked benchmark | 45.99 | 25.55 | 0
as % of all-in cost | 18.81% | 9.678% | 0%
8. Reference campus (44 MW, Base case) | Value
NPV ($m) | -15.8373
IRR | 9.136%
Break-even fee ($/kW-month) | 156.0189
Stabilised EBITDA yield on build cost | 11.62%
9. What it would take (Base supply, Targeted hub, 2030) | Value
Five-lever package (firm MW) | 805.4
Gap to minimum reserve margin (MW) | 584.2664
Gap to target reserve margin (MW) | 753.7453
Coverage of the target-margin gap (x) | 1.0685
Indicative package cost ($m/yr) | 287.1304
Reserve margin in 2030 after the package | 16.52%
Share of package supplied by data centres themselves | 19.29%
Hub's share of the target-margin gap | 20.62%

## Inputs
Inputs and assumptions
Blue = hard-coded input. Yellow fill = key lever. Tag: [S] sourced (see Sources sheet) / [A] analyst assumption. Scenario-invariant inputs are entered once in the Base column.
ID | Parameter | Unit | Stress | Base | Favourable | Tag | Source / rationale
A. Grid baseline (June 2026) |  |  | Stress | Base | Favourable
peak0 | Peak demand, June 2026 | MW | 2514 | 2514 | 2514 | [S] | S2: Kenya Power peak demand 2,514 MW in June 2026 (2,549 MW in July 2026).
rm0 | Reserve margin applied to the June 2026 peak | % | -1.5% | 3.34% | 20.73% | [S] | S3: -1.5% over the 12 months to Jun 2026 (Stress). S2: 3.34% in Jun 2026 (Base). S2: 20.73% in Jan 2026 - Favourable assumes January-level availability is restored and sustained. IEA comfortable range 20-35% (S1).
growth | Peak-demand growth per year (excluding the hub programme) | %/yr | 8% | 6.5% | 5% | [S/A] | S2: official projection c.5%/yr (Favourable). Observed: 6.4% FY24-FY25 and 8.5% FY25-Jun 2026 (S2 data) -> Base 6.5%, Stress 8%.
B. Firm, evening-capable supply additions (MW) |  |  | Stress | Base | Favourable
eth_mw | Ethiopia import uplift (200 -> 400 MW) | MW | 100 | 200 | 200 | [S/A] | S2: Ethiopia imports of 200 MW 'expected to double'; S19: PPA allows up to 400 MW. Stress assumes only half the uplift is delivered.
eth_yr | Ethiopia uplift: first year counted in annual peak | year | 2028 | 2027 | 2027 | [A] | S2 says 'from December' without a year; Base assumes Dec 2026 so 2027 is the first full peak year (conflict C3).
olk1_mw | Olkaria I rehabilitation (45 -> 61 MW) | MW | 16 | 16 | 16 | [S] | S13: +16 MW, late 2026.
olk1_yr | Olkaria I: first year counted | year | 2028 | 2027 | 2027 | [A] | S13 says late 2026 -> first full peak year 2027.
bess_mw | Battery storage (KenGen BESS), evening-firm MW | MW | 100 | 100 | 100 | [S] | S13: 100 MW battery system planned for 2027; counted at full rating for a 4-hour evening peak.
bess_yr | BESS: first year counted | year | 2028 | 2027 | 2027 | [S/A] | S13: 2027. Stress delays one year.
bess2_mw | Additional storage procured through auctions | MW | 0 | 0 | 100 | [A] | S14: BESS to be competitively sourced inside the auction framework. Only the Favourable case assumes an extra 100 MW.
bess2_yr | Additional storage: first year counted | year | 2029 | 2029 | 2029 | [A] | Earliest realistic COD given S14 timelines (auction -> PPA -> financial close -> COD).
olk7_mw | Olkaria VII geothermal | MW | 80.3 | 80.3 | 80.3 | [S] | S13: 80.3 MW under development; commissioning date not stated.
olk7_yr | Olkaria VII: first year counted | year | 2030 | 2029 | 2028 | [A] | S13 gives no date. Base assumes 2029.
solar_mw | Seven Forks solar | MW | 42.5 | 42.5 | 42.5 | [S] | S13: 42.5 MW solar.
solar_firm | Seven Forks: share counted at the evening peak | % | 0% | 0% | 0% | [A] | S2: solar output falls away as the 6-10pm peak arrives, so solar adds nothing to the evening reserve margin.
solar_yr | Seven Forks: first year counted | year | 2028 | 2028 | 2028 | [A] | Date not stated in S13; irrelevant while the evening contribution is 0%.
auction_mw | New auction-procured firm capacity, per year from the first COD year | MW/yr | 0 | 150 | 300 | [A] | S14: auctions operational within 12 months; financial close 9-12 months after PPA; COD 24-30 months after financial close -> first COD c.2030. Volume is an assumption: Stress none, Base 150 MW/yr, Favourable 300 MW/yr.
auction_yr | First COD year of auction-procured capacity | year | 2030 | 2030 | 2030 | [S/A] | Derived from the S14 timeline.
C. Data-centre demand (hub cases) |  |  | Status quo | Targeted hub | Ambitious hub
africa2030 | Africa data-centre capacity in 2030 (midpoint of 1.5-2.2 GW) | MW | 1850 | 1850 | 1850 | [S] | S12: McKinsey range 1.5-2.2 GW by 2030; midpoint used.
share | Kenya share of Africa data-centre capacity in 2030 | % | 4% | 12% | 20% | [S/A] | Status quo = Kenya's current share (c.20 MW of >500 MW, S9/S11 = 4%). Targeted = announced pipeline delivered (c.220 MW, S9). Ambitious = 20%, comparable to a clear No.2 hub.
it2026 | Kenya data-centre IT capacity, 2026 | MW | 45 | 45 | 45 | [S] | S9: almost 20 MW existing plus almost 25 MW expected by end-2025.
pue | Power usage effectiveness (PUE) | x | 1.4 | 1.4 | 1.4 | [A] | Typical 1.3-1.5 for a temperate-altitude site such as Nairobi; grid MW = IT MW x PUE.
util | Average IT utilisation (flat load at the evening peak) | % | 75% | 75% | 75% | [A] | Contracted-and-drawing share of installed IT capacity at maturity; data-centre load is near-flat so peak = average.
D. Economics |  |  | Stress | Base | Favourable
fee | Colocation infrastructure fee (ex-power) | $/kW-month | 110 | 150 | 200 | [A] | No public Kenyan price (paywalled in S9). Range spans typical wholesale-to-retail colocation. Replace with operator quotes before relying on it.
capex | Data-centre build cost | $m per IT MW | 11.3 | 8 | 7 | [S] | S21: JLL global average $11.3m/MW (Stress); emerging markets below $8m/MW (Base).
campus_mw | Average campus size | MW IT | 35 | 35 | 35 | [A] | Nxtra Tatu City is 44 MW (S10); smaller colocation sites pull the average down.
jobs | Operational jobs per campus | jobs | 100 | 150 | 200 | [S] | S22: roughly 100-200 jobs at a typical treated US county; colocation is 'modest'.
tariff | All-in grid tariff to a large data-centre customer | $/kWh | 0.11 | 0.09 | 0.065 | [S/A] | S18: KSh 7.99/kWh (2020); S16: April 2026 pass-throughs add c.KSh 4.7/kWh; S15: wholesale c.$0.07. At c.KSh 129/$ (S15 implied) the range is $0.065-0.11 (conflict C5).
eth_price | Benchmark: Ethiopia-to-Kenya wholesale price | $/kWh | 0.065 | 0.065 | 0.065 | [S] | S19: 6.5 US cents/kWh PPA price.
lcos | Cost of shifting energy through a 4-hour battery (global benchmark) | $/MWh | 78 | 78 | 78 | [S] | S23: BNEF 2025 four-hour battery LCOE.
em_prem | Emerging-market premium on storage cost | x | 1.5 | 1.5 | 1.5 | [A] | Financing, import and logistics premium over the global benchmark.
hours | Evening peak hours to cover | hours/day | 4 | 4 | 4 | [S] | S2: evening peak c.6pm-10pm.
rte | Battery round-trip efficiency | % | 85% | 85% | 85% | [A] | Typical lithium-ion utility-scale range 80-90%.
charge_price | Energy price paid to recharge the battery | $/MWh | 70 | 70 | 70 | [S] | S15: wholesale c.$0.07/kWh.
min_rm | Minimum reserve margin before connecting new hub load | % | 10% | 10% | 10% | [A] | Gate threshold. Below the IEA 20-35% comfortable range (S1) but well above the 3.3% of Jun 2026.
target_rm | Target reserve margin to restore | % | 15% | 15% | 15% | [A] | Planning target; sensitivity on the Matrix sheet.
E. Reference campus (Nxtra-scale, 44 MW in two phases)
mw1 | Phase 1 IT capacity | MW | 22 | 22 | 22 | [S] | S10: two phases of 22 MW.
mw2 | Phase 2 IT capacity | MW | 22 | 22 | 22 | [S] | S10.
ph2_off | Phase 2 starts this many years after phase 1 | years | 2 | 2 | 2 | [A] | Typical lag between phases.
wacc | Discount rate (USD, pre-tax, unlevered) | % | 10% | 10% | 10% | [A] | Hurdle for emerging-market digital infrastructure with some DFI participation. Sensitivity on UnitEconomics.
opex_pct | Variable opex (staff, maintenance, insurance, connectivity) | % of revenue | 20% | 20% | 20% | [A] | Analyst assumption.
fixed_opex | Fixed opex | $m per installed MW per year | 0.15 | 0.15 | 0.15 | [A] | Analyst assumption.
maint | Maintenance capex | % of cumulative growth capex per year | 1.5% | 1.5% | 1.5% | [A] | Analyst assumption.
tv_mult | Terminal value at end of horizon | x EBITDA | 7 | 7 | 7 | [A] | Conservative versus 15-20 year asset life; set to 0 to see the no-terminal-value case.
start_year | Campus phase 1 first operating year | year | 2027 | 2027 | 2027 | [S] | S10: ready for service Q1 2027.
F. 'What it would take' package (Base supply, Targeted hub)
lv_storage | Utility-scale 4-hour storage procured through auctions | MW | 250 | 250 | 250 | [A] | S14: BESS to be competitively sourced; S13: first 100 MW due 2027. Size is an assumption.
lv_import | Second Ethiopia import tranche (beyond the 400 MW PPA cap) | MW | 150 | 150 | 150 | [A] | S2: Ethiopia has large hydro surplus; S19: current PPA caps at 400 MW. Size is an assumption.
lv_geo | Accelerated geothermal (Olkaria VII pull-forward + mobile wellhead units) | MW | 100 | 100 | 100 | [A] | S13: wellhead units 'by 2027' (MW not stated); Olkaria VII 80.3 MW. Size is an assumption.
lv_auction | Auction tranche pulled forward one year | MW | 150 | 150 | 150 | [A] | S14: first COD c.2030 on the stated timeline; pull-forward needs procurement and financial-close discipline.
lf_import | Load factor of imported power | % | 85% | 85% | 85% | [A] | Analyst assumption for indicative energy cost.
lf_geo | Load factor of geothermal / new firm generation | % | 90% | 90% | 90% | [A] | Geothermal runs near-baseload; analyst assumption.

## Grid
Grid headroom, 2026-2032: firm evening-capable supply versus peak demand (before any hub load)
Each block is one supply scenario. Negative reserve margin = unserved peak (rationing) unless emergency capacity is bought; it measures the size of the response needed.
Stress supply case | Unit | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
Peak demand | MW | 2514 | 2715.12 | 2932.3296 | 3166.916 | 3420.2692 | 3693.8908 | 3989.402
Baseline firm available capacity (Jun 2026, incl. imports) | MW | 2476.29 | 2476.29 | 2476.29 | 2476.29 | 2476.29 | 2476.29 | 2476.29
+ Ethiopia import uplift | MW | 0 | 0 | 100 | 100 | 100 | 100 | 100
+ Olkaria I rehabilitation | MW | 0 | 0 | 16 | 16 | 16 | 16 | 16
+ Battery storage (KenGen BESS) | MW | 0 | 0 | 100 | 100 | 100 | 100 | 100
+ Additional storage (auctions) | MW | 0 | 0 | 0 | 0 | 0 | 0 | 0
+ Olkaria VII geothermal | MW | 0 | 0 | 0 | 0 | 80.3 | 80.3 | 80.3
+ Seven Forks solar (evening-firm share only) | MW | 0 | 0 | 0 | 0 | 0 | 0 | 0
+ Auction-procured firm capacity (cumulative) | MW | 0 | 0 | 0 | 0 | 0 | 0 | 0
Firm evening-capable capacity | MW | 2476.29 | 2476.29 | 2692.29 | 2692.29 | 2772.59 | 2772.59 | 2772.59
Reserve margin before hub load | % | -1.5% | -8.796% | -8.186% | -14.99% | -18.94% | -24.94% | -30.5%
Spare MW (firm capacity minus peak) | MW | -37.71 | -238.83 | -240.0396 | -474.626 | -647.6792 | -921.3008 | -1216.812
New firm MW needed each year just to hold the margin | MW/yr |  | 201.12 | 217.2096 | 234.5864 | 253.3533 | 273.6215 | 295.5113
Base supply case | Unit | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
Peak demand | MW | 2514 | 2677.41 | 2851.4417 | 3036.7854 | 3234.1764 | 3444.3979 | 3668.2837
Baseline firm available capacity (Jun 2026, incl. imports) | MW | 2597.9676 | 2597.9676 | 2597.9676 | 2597.9676 | 2597.9676 | 2597.9676 | 2597.9676
+ Ethiopia import uplift | MW | 0 | 200 | 200 | 200 | 200 | 200 | 200
+ Olkaria I rehabilitation | MW | 0 | 16 | 16 | 16 | 16 | 16 | 16
+ Battery storage (KenGen BESS) | MW | 0 | 100 | 100 | 100 | 100 | 100 | 100
+ Additional storage (auctions) | MW | 0 | 0 | 0 | 0 | 0 | 0 | 0
+ Olkaria VII geothermal | MW | 0 | 0 | 0 | 80.3 | 80.3 | 80.3 | 80.3
+ Seven Forks solar (evening-firm share only) | MW | 0 | 0 | 0 | 0 | 0 | 0 | 0
+ Auction-procured firm capacity (cumulative) | MW | 0 | 0 | 0 | 0 | 150 | 300 | 450
Firm evening-capable capacity | MW | 2597.9676 | 2913.9676 | 2913.9676 | 2994.2676 | 3144.2676 | 3294.2676 | 3444.2676
Reserve margin before hub load | % | 3.34% | 8.835% | 2.193% | -1.4% | -2.78% | -4.359% | -6.107%
Spare MW (firm capacity minus peak) | MW | 83.9676 | 236.5576 | 62.526 | -42.5178 | -89.9088 | -150.1303 | -224.0161
New firm MW needed each year just to hold the margin | MW/yr |  | 163.41 | 174.0317 | 185.3437 | 197.391 | 210.2215 | 223.8859
Favourable supply case | Unit | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
Peak demand | MW | 2514 | 2639.7 | 2771.685 | 2910.2692 | 3055.7827 | 3208.5718 | 3369.0004
Baseline firm available capacity (Jun 2026, incl. imports) | MW | 3035.1522 | 3035.1522 | 3035.1522 | 3035.1522 | 3035.1522 | 3035.1522 | 3035.1522
+ Ethiopia import uplift | MW | 0 | 200 | 200 | 200 | 200 | 200 | 200
+ Olkaria I rehabilitation | MW | 0 | 16 | 16 | 16 | 16 | 16 | 16
+ Battery storage (KenGen BESS) | MW | 0 | 100 | 100 | 100 | 100 | 100 | 100
+ Additional storage (auctions) | MW | 0 | 0 | 0 | 100 | 100 | 100 | 100
+ Olkaria VII geothermal | MW | 0 | 0 | 80.3 | 80.3 | 80.3 | 80.3 | 80.3
+ Seven Forks solar (evening-firm share only) | MW | 0 | 0 | 0 | 0 | 0 | 0 | 0
+ Auction-procured firm capacity (cumulative) | MW | 0 | 0 | 0 | 0 | 300 | 600 | 900
Firm evening-capable capacity | MW | 3035.1522 | 3351.1522 | 3431.4522 | 3531.4522 | 3831.4522 | 4131.4522 | 4431.4522
Reserve margin before hub load | % | 20.73% | 26.95% | 23.8% | 21.34% | 25.38% | 28.76% | 31.54%
Spare MW (firm capacity minus peak) | MW | 521.1522 | 711.4522 | 659.7672 | 621.1829 | 775.6695 | 922.8804 | 1062.4518
New firm MW needed each year just to hold the margin | MW/yr |  | 125.7 | 131.985 | 138.5842 | 145.5135 | 152.7891 | 160.4286

## Hub
Data-centre demand and the size of the prize, 2026-2032
Kenya IT capacity moves linearly from 2026 to the 2030 target (share of Africa capacity) and keeps that pace afterwards. Grid load counts only capacity above the Status quo case, because Status quo growth is already inside the peak-demand growth rate.
Status quo | Unit | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
Kenya data-centre IT capacity | MW IT | 45 | 52.25 | 59.5 | 66.75 | 74 | 81.25 | 88.5
IT capacity above Status quo | MW IT | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hub load on the grid at the evening peak | MW | 0 | 0 | 0 | 0 | 0 | 0 | 0
Infrastructure-fee revenue pool (Base fee) | $m/yr | 60.75 | 70.5375 | 80.325 | 90.1125 | 99.9 | 109.6875 | 119.475
Cumulative build investment since 2026 (Base cost) | $m | 0 | 58 | 116 | 174 | 232 | 290 | 348
Targeted hub | Unit | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
Kenya data-centre IT capacity | MW IT | 45 | 89.25 | 133.5 | 177.75 | 222 | 266.25 | 310.5
IT capacity above Status quo | MW IT | 0 | 37 | 74 | 111 | 148 | 185 | 222
Hub load on the grid at the evening peak | MW | 0 | 38.85 | 77.7 | 116.55 | 155.4 | 194.25 | 233.1
Infrastructure-fee revenue pool (Base fee) | $m/yr | 60.75 | 120.4875 | 180.225 | 239.9625 | 299.7 | 359.4375 | 419.175
Cumulative build investment since 2026 (Base cost) | $m | 0 | 354 | 708 | 1062 | 1416 | 1770 | 2124
Ambitious hub | Unit | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
Kenya data-centre IT capacity | MW IT | 45 | 126.25 | 207.5 | 288.75 | 370 | 451.25 | 532.5
IT capacity above Status quo | MW IT | 0 | 74 | 148 | 222 | 296 | 370 | 444
Hub load on the grid at the evening peak | MW | 0 | 77.7 | 155.4 | 233.1 | 310.8 | 388.5 | 466.2
Infrastructure-fee revenue pool (Base fee) | $m/yr | 60.75 | 170.4375 | 280.125 | 389.8125 | 499.5 | 609.1875 | 718.875
Cumulative build investment since 2026 (Base cost) | $m | 0 | 650 | 1300 | 1950 | 2600 | 3250 | 3900
2030 prize and cost, by hub case | Unit | Status quo | Targeted hub | Ambitious hub
Kenya IT capacity in 2030 | MW IT | 74 | 222 | 370
Share of Africa capacity in 2030 | % | 4% | 12% | 20%
Infrastructure-fee revenue pool, 2030 | $m/yr | 99.9 | 299.7 | 499.5
Build investment 2026-2030 | $bn | 0.232 | 1.416 | 2.6
Campuses at average size | count | 2.1143 | 6.3429 | 10.5714
Operational jobs (base jobs per campus) | jobs | 317.1429 | 951.4286 | 1585.7143
Hub load added to the grid, 2030 | MW | 0 | 155.4 | 310.8
Cost to firm 1 MW of evening peak with 4-hour storage | $ per MW-yr | 188855.2941 | 188855.2941 | 188855.2941
Hub-attributable firming cost, 2030 | $m/yr | 0 | 29.3481 | 58.6962
Firming cost as % of infrastructure-fee revenue | % | 0% | 9.792% | 11.75%
Energy drawn by the whole data-centre estate, 2030 | TWh/yr | 0.68065 | 2.042 | 3.4033
Cross-check: projected Kenya data-centre market in 2031 (S7) | $m | 805 | 805 | 805
Top-down market / bottom-up fee pool (2031 vs 2030) | x | 8.0581 | 2.686 | 1.6116
Note on C37: S7: Kenya DC market projected at $805m by 2031. Likely a broader definition than infrastructure fees (includes cloud/services).
Note on D37: S7: Kenya DC market projected at $805m by 2031. Likely a broader definition than infrastructure fees (includes cloud/services).
Note on E37: S7: Kenya DC market projected at $805m by 2031. Likely a broader definition than infrastructure fees (includes cloud/services).

## Matrix
Supply scenario x hub ambition: reserve margin, firm-MW gap and connectable load
Reserve margin = (firm capacity - peak - hub load) / (peak + hub load).
Supply case | Hub case | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
Stress | Status quo | -1.5% | -8.796% | -8.186% | -14.99% | -18.94% | -24.94% | -30.5%
Stress | Targeted hub | -1.5% | -10.08% | -10.56% | -18% | -22.46% | -28.69% | -34.34%
Stress | Ambitious hub | -1.5% | -11.33% | -12.81% | -20.82% | -25.69% | -32.08% | -37.77%
Base | Status quo | 3.34% | 8.835% | 2.193% | -1.4% | -2.78% | -4.359% | -6.107%
Base | Targeted hub | 3.34% | 7.279% | -0.518% | -5.044% | -7.237% | -9.465% | -11.72%
Base | Ambitious hub | 3.34% | 5.766% | -3.089% | -8.429% | -11.3% | -14.05% | -16.69%
Favourable | Status quo | 20.73% | 26.95% | 23.8% | 21.34% | 25.38% | 28.76% | 31.54%
Favourable | Targeted hub | 20.73% | 25.11% | 20.43% | 16.67% | 19.32% | 21.41% | 23.02%
Favourable | Ambitious hub | 20.73% | 23.32% | 17.23% | 12.35% | 13.81% | 14.86% | 15.55%
Reserve margin in 2030 | Supply case \ Hub case | Status quo | Targeted hub | Ambitious hub
| Stress | -18.94% | -22.46% | -25.69%
| Base | -2.78% | -7.237% | -11.3%
| Favourable | 25.38% | 19.32% | 13.81%
Firm MW needed in 2030 to reach the minimum reserve margin | Supply case \ Hub case | Status quo | Targeted hub | Ambitious hub
| Stress | 989.7062 | 1160.6462 | 1331.5862
| Base | 413.3264 | 584.2664 | 755.2064
| Favourable | 0 | 0 | 0
Firm MW needed in 2030 to reach the target reserve margin | Supply case \ Hub case | Status quo | Targeted hub | Ambitious hub
| Stress | 1160.7196 | 1339.4296 | 1518.1396
| Base | 575.0353 | 753.7453 | 932.4553
| Favourable | 0 | 0 | 40.1179
Storage (MWh, 4-hour) to carry the hub's own evening load in 2030 | Supply case \ Hub case | Status quo | Targeted hub | Ambitious hub
| Stress | 0 | 621.6 | 1243.2
| Base | 0 | 621.6 | 1243.2
| Favourable | 0 | 621.6 | 1243.2
Connectable new data-centre IT capacity (MW) while keeping the minimum reserve margin | Supply case | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
| Stress | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Base | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Favourable | 233.5517 | 387.4305 | 331.2543 | 285.8494 | 407.0054 | 521.2322 | 628.1833
Connectable new data-centre IT capacity (MW) at the target reserve margin | Supply case | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
| Stress | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Base | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Favourable | 119.2979 | 261.2813 | 202.0824 | 152.9131 | 262.7761 | 365.7098 | 461.3679

## UnitEconomics
Unit economics: what a tenant pays, and whether a reference campus clears its hurdle
Part 1 is a tenant's all-in cost per IT kW-month. Part 2 is an illustrative pre-tax, unlevered campus case; every driver is an input.
Part 1. Tenant cost per IT kW-month | Unit | Stress | Base | Favourable | Ethiopia-linked benchmark
Infrastructure fee | $/kW-month | 110 | 150 | 200 | 150
Grid power (PUE x 730 h x all-in tariff) | $/kW-month | 112.42 | 91.98 | 66.43 | 66.43
Evening self-supply premium (storage shifting cost, per IT kW) | $/kW-month | 22.0331 | 22.0331 | 22.0331 | 22.0331
All-in tenant cost | $/kW-month | 244.4531 | 264.0131 | 288.4631 | 238.4631
Power (grid + evening premium) as % of all-in cost | % | 55% | 43.18% | 30.67% | 37.1%
Power-price gap to the Ethiopia-linked benchmark (grid power only) | $/kW-month | 45.99 | 25.55 | 0
...as % of the tenant's all-in cost | % | 18.81% | 9.678% | 0%
Part 2. Reference campus cash flow (Base case, $m unless stated) | Unit | t=0 | t=1 | t=2 | t=3 | t=4 | t=5 | t=6 | t=7 | t=8 | t=9 | t=10 | t=11
Period index t |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
Calendar year |  | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
Installed IT capacity | MW | 22 | 22 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
Contracted IT load (input ramp) | MW | 8 | 15 | 22 | 28 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33
Contracted IT load (capped at installed) | MW | 8 | 15 | 22 | 28 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33
Infrastructure-fee revenue | $m | 14.4 | 27 | 39.6 | 50.4 | 59.4 | 59.4 | 59.4 | 59.4 | 59.4 | 59.4 | 59.4 | 59.4
Variable opex | $m | -2.88 | -5.4 | -7.92 | -10.08 | -11.88 | -11.88 | -11.88 | -11.88 | -11.88 | -11.88 | -11.88 | -11.88
Fixed opex | $m | -3.3 | -3.3 | -6.6 | -6.6 | -6.6 | -6.6 | -6.6 | -6.6 | -6.6 | -6.6 | -6.6 | -6.6
EBITDA | $m | 8.22 | 18.3 | 25.08 | 33.72 | 40.92 | 40.92 | 40.92 | 40.92 | 40.92 | 40.92 | 40.92 | 40.92
Growth capacity added (MW) | MW | 22 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Growth capex | $m | -176 | 0 | -176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative growth MW at start of period | MW | 0 | 22 | 22 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
Maintenance capex | $m | 0 | -2.64 | -2.64 | -5.28 | -5.28 | -5.28 | -5.28 | -5.28 | -5.28 | -5.28 | -5.28 | -5.28
Terminal value (multiple of final-year EBITDA) | $m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 286.44
Pre-tax unlevered cash flow | $m | -167.78 | 15.66 | -153.56 | 28.44 | 35.64 | 35.64 | 35.64 | 35.64 | 35.64 | 35.64 | 35.64 | 322.08
Linear decomposition (NPV is linear in fee and in capex per MW) | Unit | t=0 | t=1 | t=2 | t=3 | t=4 | t=5 | t=6 | t=7 | t=8 | t=9 | t=10 | t=11
Fee-linked cash flow per $1/kW-month of fee | $m | 0.0768 | 0.144 | 0.2112 | 0.2688 | 0.3168 | 0.3168 | 0.3168 | 0.3168 | 0.3168 | 0.3168 | 0.3168 | 2.5344
Fixed-opex cash flow (incl. terminal value effect) | $m | -3.3 | -3.3 | -6.6 | -6.6 | -6.6 | -6.6 | -6.6 | -6.6 | -6.6 | -6.6 | -6.6 | -52.8
Capex cash flow per $1m of build cost per MW | $m | -22 | -0.33 | -22.33 | -0.66 | -0.66 | -0.66 | -0.66 | -0.66 | -0.66 | -0.66 | -0.66 | -0.66
Results (Base case) | Unit | 0 2027: Value
NPV at the base discount rate | $m | 0 2027: -15.8373
IRR (pre-tax, unlevered, incl. terminal value) | % | 0 2027: 9.136%
NPV with no terminal value | $m | 0 2027: -116.2328
NPV change per +$1/kW-month of fee | $m | 0 2027: 2.6313
NPV excluding fee and capex effects (fixed opex) | $m | 0 2027: -59.3602
NPV change per +$1m/MW of build cost | $m | 0 2027: -43.8958
Break-even fee at Base build cost (NPV = 0) | $/kW-month | 0 2027: 156.0189
Check: linear decomposition reproduces NPV (should be 0) | $m | 0 2027: 0
Stabilised EBITDA yield on build cost (final year) | % | 0 2027: 11.62%
NPV ($m): infrastructure fee ($/kW-month, down) x build cost ($m per MW, across) | Fee \ Build cost | bar: 0 2027 to 5 2032
|  | 6 | 7 | 8 | 9 | 10 | 11.3
| 110 | 0 2027: -33.2962; 1 2028: -77.192; 2 2029: -121.0878; 3 2030: -164.9837; 4 2031: -208.8795; 5 2032: -265.9441
| 130 | 0 2027: 19.3291; 1 2028: -24.5667; 2 2029: -68.4626; 3 2030: -112.3584; 4 2031: -156.2542; 5 2032: -213.3188
| 150 | 0 2027: 71.9544; 1 2028: 28.0585; 2 2029: -15.8373; 3 2030: -59.7331; 4 2031: -103.629; 5 2032: -160.6935
| 175 | 0 2027: 137.736; 1 2028: 93.8401; 2 2029: 49.9443; 3 2030: 6.0485; 4 2031: -37.8474; 5 2032: -94.9119
| 200 | 0 2027: 203.5176; 1 2028: 159.6217; 2 2029: 115.7259; 3 2030: 71.8301; 4 2031: 27.9342; 5 2032: -29.1303
| 225 | 0 2027: 269.2992; 1 2028: 225.4033; 2 2029: 181.5075; 3 2030: 137.6117; 4 2031: 93.7158; 5 2032: 36.6513
| Break-even fee | 0 2027: 122.6541; 1 2028: 139.3365; 2 2029: 156.0189; 3 2030: 172.7013; 4 2031: 189.3837; 5 2032: 211.0709
NPV ($m) at different discount rates (Base fee and build cost) | Rate | 0 2027: NPV
| 8% | 0 2027: 23.0778
| 10% | 0 2027: -15.8373
| 12% | 0 2027: -47.6089
| 14% | 0 2027: -73.6373
Note on A17: [A] Analyst assumption: ramp to c.75% of 44 MW by year 5 (matches Inputs 'util').

## Levers
What it would take: five levers sized against the 2030 firm-capacity gap (Base supply, Targeted hub)
Costs are indicative annual procurement costs, not a budget. Lever sizes are inputs on the Inputs sheet (section F).
Lever | Unit | Firm MW | Lead time | Evidence / basis | Tag | Indicative cost ($m/yr)
1. Data centres bring their own evening power (on-site storage) | MW | 155.4 | Built with each campus (12-18 months) | S2: evening peak 6-10pm; sized at the Targeted-hub load added in 2030. Cost borne by tenants. | [A] | 29.3481
2. Utility-scale 4-hour storage via auctions | MW | 250 | 24-30 months after financial close (S14) | S13 first 100 MW in 2027; S14 BESS inside the auction framework. | [A] | 47.2138
3. Second Ethiopia import tranche | MW | 150 | 12-24 months (existing interconnector) | S2 / S19: 200 MW now, 400 MW PPA cap, large Ethiopian hydro surplus. Priced at the 6.5 c/kWh PPA benchmark. | [A] | 72.5985
4. Accelerated geothermal (Olkaria VII, wellhead units) | MW | 100 | 12-36 months (S13: wellhead units by 2027) | S13: Olkaria VII 80.3 MW; mobile wellhead units. Priced at wholesale $0.07/kWh (S15). | [A] | 55.188
5. Auction tranche pulled forward one year | MW | 150 | Needs auction live by late 2026 (S14) | S14: first COD c.2030; this lever brings one tranche to 2029. Priced at wholesale $0.07/kWh. | [A] | 82.782
Package total |  | 805.4 |  |  |  | 287.1304
Coverage of the 2030 gap | Unit | Value
Gap to the minimum reserve margin (Base supply, Targeted hub, 2030) | MW | 584.2664
Gap to the target reserve margin (Base supply, Targeted hub, 2030) | MW | 753.7453
Package coverage of the minimum-margin gap | x | 1.3785
Package coverage of the target-margin gap | x | 1.0685
Reserve margin in 2030 after the package (Base supply, Targeted hub) | % | 16.52%
Share of the package supplied by the data centres themselves (lever 1) | % | 19.29%
Share of the target-margin gap attributable to the hub (hub load / gap) | % | 20.62%

## Screen
Beyond data centres: which energy-intensive industries fit Kenya's grid shape?
Scores 1-5 are analyst JUDGEMENT [J], not data. Change the blue weights and scores to test the ranking; the equal-weight ranking shows how much the weights matter.
Industry | Fit with an evening-constrained grid (load flexibility) | Market pull evidence | Kenya's input advantage | Jobs per MW | Speed to deploy | Weighted score | Rank | Equal-weight rank | Equal-weight mean
Weight | 30% | 20% | 20% | 15% | 15% | 100%
Agro-processing and cold chain | 4 | 4 | 4 | 5 | 5 | 4.3 | 1 | 1 | 4.4
Night-shift heavy industry (cement, steel recycling, glass) | 5 | 4 | 3 | 4 | 4 | 4.1 | 2 | 2 | 4
Textiles and apparel in export zones | 3 | 3 | 3 | 5 | 4 | 3.45 | 3 | 3 | 3.6
Flexible / batch compute (AI training, rendering) | 5 | 3 | 3 | 1 | 3 | 3.3 | 4 | 6 | 3
EV and battery assembly, smart charging | 4 | 3 | 3 | 3 | 3 | 3.3 | 5 | 4 | 3.2
Cloud and colocation data centres | 2 | 5 | 4 | 2 | 3 | 3.15 | 6 | 4 | 3.2
Green hydrogen / ammonia (electrolysis) | 5 | 2 | 3 | 2 | 1 | 2.95 | 7 | 7 | 2.6
Why these criteria: Kenya's binding constraint is firm power at 6-10pm (S2). Loads that can move off that window, or store their own evening energy, use the grid's idle hours (night tariff uptake +74% in H2 2025, S17) instead of competing for its scarcest ones.

## Sources
Source register and conflicts
Figures read on 2026-10-19. Press and trade-press sources: confirm against EPRA / Kenya Power primary releases before publication.
ID | Source | Date | URL | What the model takes from it
S1 | Business Daily - Kenya risks electricity cuts as reserve shrinks to 3.3pc | 2026-08-26 | https://www.businessdailyafrica.com/bd/corporate/industry/kenya-risks-electricity-cuts-as-reserve-shrinks-to-3-3pc-5572288 | Reserve margin below 3.3%; IEA comfortable range of 20-35%; State of the Grid briefing 11 Aug 2026
S2 | TechTrends KE - Kenya electricity rationing risk | 2026-08-27 | https://techtrendske.co.ke/2026/08/27/kenya-electricity-rationing-risk/ | Peak demand series (2,177 / 2,316 / 2,514 / 2,549 MW); reserve margin 20.73% (Jan 2026) to 3.34% (Jun 2026); Ethiopia imports 200 MW expected to double; evening peak c.6-10pm; wind+solar >20% of capacity; little battery storage
S3 | Business Daily - How Kenya teetered on the brink of widespread power rationing | 2026-09-24 | https://www.businessdailyafrica.com/bd/corporate/industry/how-kenya-teetered-on-the-brink-of-widespread-power-rationing-5607180 | Reserve margin of -1.5% over the 12 months to June 2026 (headline figure only; article body did not load)
S4 | Business Daily - Kenya electricity imports rise further to avert rationing | 2026-08-30 | https://www.businessdailyafrica.com/bd/corporate/industry/kenya-electricity-imports-rise-further-to-avert-rationing-5575112 | Imports 12% of Kenya Power supply in H1 2026 vs 10% in H1 2025 (Ethiopia, Uganda)
S5 | Capital FM / AllAfrica - Kenya tops East Africa in power demand and renewables (EPRA 2025 statistics) | 2025-10-23 | https://capitalfm.africa/kenya-tops-east-africa-renewable-energy-generation-epra-report/ | Renewable share 80.17%; geothermal 940 MW; installed capacity 3,192 MW; peak demand 2,316 MW (2025)
S6 | The Star - Kenya's renewable energy generation mix | 2026-04-09 | https://www.the-star.co.ke/news/infographics/2026-04-09-kenyas-renewable-energy-generation-mix | Jul-Dec 2025 mix: geothermal 40.06%, thermal 9.11%, imports 12.10%, renewables 78.79%
S7 | Semafor - Energy shortfall 'problem' scuppers Kenya's $1B Microsoft data center | 2026-05-06 | https://semafor.com/article/05/06/2026/energy-shortfall-problem-scuppers-kenyas-1b-microsoft-data-center | Microsoft/G42 Olkaria project unlikely to proceed; President Ruto: power capacity inadequate; 10,000 MW by 2030 target; Kenya DC market projected at $805m by 2031; Nxtra 44 MW at Tatu City
S8 | Citizen Digital - Kenya's $1B Microsoft data centre project in limbo over power concerns | 2026-05-23 | https://citizen.digital/article/kenyas-1b-microsoft-data-centre-project-in-limbo-over-power-concerns-n383281 | Government says project not abandoned; Ruto: one data centre requires 1,000 MW; daily load-shedding 5-10pm (Nov 2025); target at least 10,000 MW by 2030, >KSh 1 trillion
S9 | BusinessWire / ResearchAndMarkets - Kenya Colocation Data Center Portfolio Analysis 2025 | 2025-06-18 | https://www.businesswire.com/news/home/20250618339125/en/Kenya-Colocation-Data-Center-Portfolio-Analysis-Report-2025-Detailed-Analysis-of-13-Existing-Data-Centers-and-9-Upcoming-Data-Centers---ResearchAndMarkets.com | Existing IT capacity almost 20 MW; upcoming c.200 MW; almost 25 MW more by end-2025; 13 existing and 9 upcoming facilities
S10 | Connecting Africa - Airtel breaks ground on 44MW data center in Nairobi | 2025-09 | https://www.connectingafrica.com/data-centers/airtel-breaks-ground-on-44mw-data-center-in-nairobi | Nxtra by Airtel, Tatu City: 44 MW in two 22 MW phases; ready for service Q1 2027
S11 | Nairametrics - Africa's data centre capacity exceeds 500 MW with 890 MW in pipeline (Fortren & Company) | 2026-07-27 | https://nairametrics.com/2026/07/27/africas-data-centre-capacity-exceeds-500-mw-with-890-mw-in-pipeline-report/ | Africa >500 MW operational, 890 MW pipeline; South Africa >60% of operational capacity; Teraco Isando 70 MW; Lagos campus 36 MW
S12 | Morocco World News - McKinsey: Africa has entered a high-speed race to expand data center capacity by 2030 | 2025-11 | https://www.moroccoworldnews.com/2025/11/269877/mckinsey-africa-has-entered-high-speed-race-to-expand-data-center-capacity-by-2030/ | Africa c.0.4 GW installed today, 1.5-2.2 GW by 2030; $10-20bn investment; >30 outages a month in some markets; uneven connectivity
S13 | SolarQuarter - KenGen to add 253 MW renewable energy to Kenya's grid by 2027 | 2026-02-24 | https://solarquarter.com/2026/02/24/kengen-to-add-253-mw-renewable-energy-to-kenyas-grid-by-2027/ | Olkaria I rehab +16 MW (late 2026); Olkaria VII 80.3 MW; Seven Forks solar 42.5 MW; 100 MW BESS in 2027; headline 253 MW
S14 | Bowmans - Kenya turns the lights back on: PPA moratorium lifted | 2025-12-03 | https://bowmanslaw.com/insights/kenya-turns-the-lights-back-on-power-purchase-agreements-moratorium-lifted/ | Auctions to be operational within 12 months; financial close 9-12 months after PPA; COD 24-30 months after financial close; BESS procurement; independent IPP office within 24 months
S15 | The Kenya Times - MPs vote to lift ban on electricity purchase deals | 2025-11-13 | https://thekenyatimes.com/latest-kenya-times-news/boost-for-kenya-power-as-mps-vote-to-lift-ban-on-electricity-purchase-deals-what-it-means/ | Vote on 12 Nov 2025; record peak 2,362 MW on 25 Jul 2025; Trade CS cites wholesale c.$0.07 (KSh 9.04) per kWh; Ethiopia imports 200 MW
S16 | Capital FM - Electricity bills set to rise as EPRA introduces new April 2026 charges | 2026-04 | https://capitalfm.africa/electricity-bills-set-to-rise-as-epra-introduces-new-april-2026-charges/ | Fuel Energy Cost Charge KSh 3.47/kWh; forex adjustment KSh 1.2341/kWh (April 2026 gazette)
S17 | Business Daily - Off-peak power saves firms Sh971m as uptake of night tariff jumps | 2026-04-05 | https://www.businessdailyafrica.com/bd/corporate/industry/off-peak-power-saves-firms-sh971m-uptake-night-tariff-jumps-5412322 | Time-of-use tariff gives 50% off-peak discount; 148 GWh used in H2 2025 (+74%); KSh 971m saved
S18 | Business Daily - Energy regulator cuts power costs for large users by 20 percent | 2020-02-24 | https://www.businessdailyafrica.com/bd/economy/energy-regulator-cuts-power-costs-for-large-users-by-20-percent-2281418 | Large-user tariff cut from KSh 10.10 to KSh 7.99 per kWh (2020 - dated; used only as a floor reference)
S19 | The Reporter Ethiopia - With surplus power, Ethiopia exports more electricity to neighbours | 2022-08-20 | https://www.thereporterethiopia.com/25841/ | Ethiopia-Kenya PPA: up to 400 MW (200 MW for first five years) at 6.5 US cents/kWh
S20 | ATC News - Mombasa: East Africa's primary digital gateway | 2026-09-07 | https://atcnews.org/mombasa-east-africas-primary-digital-gateway/ | Seven operational subsea systems rising to nine by 2027; >95% of Kenya's international traffic lands at Mombasa
S21 | Datacentres.com - Data centre construction costs rise to $11.3M per MW in 2026 (JLL) | 2026-05-12 | https://www.datacentres.com/news/data-centre-construction-costs-11m-per-mw | Global average build cost $11.3m/MW (2026); emerging markets below $8m/MW
S22 | Brookings - New evidence on data center employment effects | 2026-08 (updated) | https://www.brookings.edu/articles/new-evidence-on-data-center-employment-effects/ | Roughly 100-200 jobs at a typical treated US county; colocation = modest operational employment
S23 | Carbon Credits - Renewables plus storage surge as battery costs drop to record low (BNEF) | 2026 | https://carboncredits.com/?p=41914 | BNEF global benchmark: four-hour battery storage LCOE $78/MWh in 2025, down 27% year on year
S24 | Bowmans - Kenya data centre establishment and service contracts | n.d. | https://bowmanslaw.com/insights/kenya-data-centre-establishment-and-service-contracts-legal-and-commercial-insights/ | No single data-centre law; Data Protection Act 2019; Cloud Policy 2024 promotes localisation of sensitive data; SEZ Authority can consolidate approvals
S25 | Business Daily - Kenya races to relax rule on cheaper night tariff for factories | 2025 | https://www.businessdailyafrica.com/bd/economy/kenya-races-to-relax-rule-on-cheaper-night-tariff-for-factories-4781552 | Energy CS: government racing to relax conditions that hamper night-tariff uptake by large industry
S26 | Nation - Kenya Power takes biggest sales fall from industrial users | 2025 | https://beta.nation.co.ke/kenya/business/companies/kenya-power-takes-biggest-sales-fall-from-industrial-users-5282278 | Large-industrial revenue KSh 106.5bn in FY to June 2025, down 9.5% on KSh 117.7bn
S28 | Shega - Ethiopia raises power tariffs for crypto miners in new cost-recovery drive | 2025-10-29 | https://shega.co/news/ethiopia-raises-power-tariffs-for-crypto-miners-in-new-cost-recovery-drive | From 1 Dec, time-of-use and availability-based tariffs replace Ethiopia's old flat rate for crypto miners (rates not retrieved)
S27 | TimesLive / MEA Tech Watch - Morocco to build 500MW renewable-powered data centre in Dakhla | 2025-07-10 | https://www.timeslive.co.za/news/africa/2025-07-10-morocco-to-build-data-centre-powered-by-renewable-energy/ | Reported plan for a 500 MW renewable-powered data centre campus at Dakhla (headline-level; not independently verified)
ID | Conflict between sources |  |  | How the model resolves it
C1 | Installed capacity: EPRA 3,192 MW (S5) vs 'about 3,000 MW' (S7) vs 'whole country has 2,300 MW' and 'peak crossed 3,000 MW' (S8) |  |  | Model uses EPRA/Kenya Power series: peak demand 2,514 MW (Jun 2026) and reserve margin 3.34% (S2). The 2,300 MW and 3,000 MW remarks are political shorthand and are not used.
C2 | Nxtra Tatu City completion: 'this year' (S7) vs ready for service Q1 2027 (S10) |  |  | Model uses Q1 2027 (S10) as the more specific, company-sourced date.
C3 | Ethiopia import uplift 'expected to double from December' (S2) with no year given |  |  | Base case assumes December 2026 (available in 2027 annual peak); Stress case halves the uplift and delays it to 2028.
C4 | Peak-demand growth: official projection of c.5% a year (S2) vs observed 6.4% (FY25) and 8.5% (FY25 to Jun 2026) from S2 data |  |  | Base case uses 6.5%; Favourable uses the official 5%; Stress uses 8%.
C5 | Large-user tariff KSh 7.99/kWh is from 2020 (S18); April 2026 pass-through charges add c.KSh 4.7/kWh (S16) |  |  | Model treats the all-in tariff as a range ($0.065 favourable / $0.09 base / $0.11 stress) rather than quoting a single current rate.
C6 | Ruto's remark that one data centre needs 1,000 MW (S7, S8) is an upper-bound political statement about the full Microsoft/G42 campus |  |  | Not used as a model input. Model sizes data-centre load from IT capacity, PUE and utilisation instead.

## Checks
Model integrity checks
All checks should read TRUE.
Check | Result
Base reserve margin reproduces the sourced 3.34% in 2026 | TRUE
Hub Targeted IT capacity in 2030 equals share x Africa 2030 capacity | TRUE
Hub Status quo adds no incremental grid load | TRUE
Campus NPV linear decomposition reproduces NPV | TRUE
Reserve margin matrix, Base supply / Status quo equals Grid reserve margin in 2030 | TRUE
Stress supply is never better than Base in 2030 (no hub) | TRUE
Base supply is never better than Favourable in 2030 (no hub) | TRUE
Tenant all-in cost equals sum of components (Base) | TRUE
Screen weights sum to 100% | TRUE
Levers: package MW equals sum of lever rows | TRUE
All checks pass | TRUE